## lng2011toPresentFields
Liquefied Natural Gas (LNG) Facilities Incidents for 2011 - present (PHMSA Form 7100.3 (Rev. 10-2014) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | DATE | Data as of date | Not on the form
SIGNIFICANT | VARCHAR2 | Identify if record meets the significant criteria or not: If there was fatality, injury, or total property damage is $50K or more in 1984 dollars, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | VARCHAR2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury then SERIOUS = ‘YES’ else SERIOUS = ’NO’. | Not on the form
REPORT_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report | Top of first page
SUPPLEMENTAL_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report submission | Top of first page
REPORT_RECEIVED_DATE | DATE | Date when Original Report submitted | Top of first page
REPORT_TYPE | VARCHAR2 | Report Type (Original, Supplemental, Final) | PART A – KEY REPORT INFORMATION
OPERATOR_ID | VARCHAR2 | Operator's OPS-issued Operator Identification number | PART A – KEY REPORT INFORMATION
NAME | VARCHAR2 | Operator Name | PART A – KEY REPORT INFORMATION
OPERATOR_STREET_ADDRESS | VARCHAR2 | Operator Address - Street | PART A – KEY REPORT INFORMATION
OPERATOR_CITY_NAME | VARCHAR2 | Operator Address - City | PART A – KEY REPORT INFORMATION
OPERATOR_STATE_ABBREVIATION | VARCHAR2 | Operator Address - State | PART A – KEY REPORT INFORMATION
OPERATOR_POSTAL_CODE | VARCHAR2 | Operator Address - Zip | PART A – KEY REPORT INFORMATION
LOCAL_DATETIME | DATE | Local time (24-hr clock) and date of the Incident | PART A – KEY REPORT INFORMATION
IYEAR | NUMBER | Year Incident occurred, derived from Incident date | Not on the form
NRC_RPT_NUM | VARCHAR2 | National Response Center Report Number | PART A – KEY REPORT INFORMATION
NRC_RPT_DATETIME | DATE | National Response Center time and date of initial telephonic report | PART A – KEY REPORT INFORMATION
UNINTENTIONAL_RELEASE_IND | VARCHAR2 | Incident resulted from - Unintentional release of commodity (Yes/No) | PART A – KEY REPORT INFORMATION
INTENTIONAL_RELEASE_IND | VARCHAR2 | Incident resulted from - Intentional release of commodity (Yes/No) | PART A – KEY REPORT INFORMATION
EMERGENCY_SHUTDOWN_IND | VARCHAR2 | Incident resulted from - Emergency shutdown (Yes/No) | PART A – KEY REPORT INFORMATION
RESULTED_FROM_OTHER_IND | NUMBER | Incident resulted from - Other reason (Yes/No) | PART A – KEY REPORT INFORMATION
RESULTED_FROM_OTHER_DETAILS | NUMBER | Incident resulted from - Other reason Details | PART A – KEY REPORT INFORMATION
COMMODITY_RELEASED_TYPE | NUMBER | Type of Commodity released | PART A – KEY REPORT INFORMATION
COMMODITY_DETAILS | NUMBER | Sub type of commodity released - Name of Other Sub-type | PART A – KEY REPORT INFORMATION
UNINTENTIONAL_RELEASE | NUMBER | Estimated volume of commodity released unintentionally in Thousand Cubic Feet (MCF) | PART A – KEY REPORT INFORMATION
INTENTIONAL_RELEASE | NUMBER | Estimated volume of intentional and controlled release/blowdown in Thousand Cubic Feet (MCF) | PART A – KEY REPORT INFORMATION
VOLUME_TO_GROUND | VARCHAR2 | Estimated volume of liquid spilled to the ground in Barrels | PART A – KEY REPORT INFORMATION
FATALITY_IND | NUMBER | Fatalities (Yes, No) | PART A – KEY REPORT INFORMATION
NUM_EMP_FATALITIES | NUMBER | Number of Fatalities of Operator Employees | PART A – KEY REPORT INFORMATION
NUM_CONTR_FATALITIES | NUMBER | Number of Fatalities of Contractor Employees working for the Operator | PART A – KEY REPORT INFORMATION
NUM_ER_FATALITIES | NUMBER | Number of Fatalities of Non-Operator emergency responders | PART A – KEY REPORT INFORMATION
NUM_GP_FATALITIES | NUMBER | Number of Fatalities of General Public | PART A – KEY REPORT INFORMATION
FATAL | NUMBER | Total number of Fatalities | PART A – KEY REPORT INFORMATION
INJURY_IND | NUMBER | Injuries (Yes, No) | PART A – KEY REPORT INFORMATION
NUM_EMP_INJURIES | NUMBER | Number of Injuries of Operator Employees | PART A – KEY REPORT INFORMATION
NUM_CONTR_INJURIES | NUMBER | Number of Injuries of Contractor Employees working for the Operator | PART A – KEY REPORT INFORMATION
NUM_ER_INJURIES | NUMBER | Number of Injuries of Non-Operator emergency responders | PART A – KEY REPORT INFORMATION
NUM_GP_INJURIES | NUMBER | Number of Injuries of General Public | PART A – KEY REPORT INFORMATION
INJURE | NUMBER | Total number of Injuries | PART A – KEY REPORT INFORMATION
SHUTDOWN_DUE_ACCIDENT_IND | NUMBER | The pipeline/facility shutdown due to the Incident (Yes, No, Null) | PART A – KEY REPORT INFORMATION
SHUTDOWN_EXPLAIN | VARCHAR2 | Explain No shutdown | PART A – KEY REPORT INFORMATION
SHUTDOWN_DATETIME | VARCHAR2 | The pipeline/facility shutdown due to the Incident - Local time and date of shutdown | PART A – KEY REPORT INFORMATION
RESTART_DATETIME | DATE | The pipeline/facility shutdown due to the Incident - Local time pipeline/facility restarted | PART A – KEY REPORT INFORMATION
STILL_SHUTDOWN_IND | DATE | The pipeline/facility shutdown due to the Incident - Still shut down (Yes, Null) | PART A – KEY REPORT INFORMATION
IGNITE_IND | VARCHAR2 | Commodity ignite (Yes, No) | PART A – KEY REPORT INFORMATION
EXPLODE_IND | VARCHAR2 | Commodity explode (Yes, No) | PART A – KEY REPORT INFORMATION
NUM_PUB_EVACUATED | VARCHAR2 | Number of general public evacuated | PART A – KEY REPORT INFORMATION
NUM_OPER_AND_CONTRACTOR_EVAC | NUMBER | Number of operator/contractor personnel evacuated | PART A – KEY REPORT INFORMATION
FACILITY_NAME | VARCHAR2 | Name of LNG Plant / Facility | PART B – ADDITIONAL FACILITY INFORMATION
NPMS_LNG_ID | VARCHAR2 | National Pipeline Mapping System (NPMS) LNG ID | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_STATUS | VARCHAR2 | Plant / Facility Status | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_LATITUDE | VARCHAR2 | Plant / Facility Location - Latitude | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_LONGITUDE | VARCHAR2 | Plant / Facility Location - Longitude | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_STATE | VARCHAR2 | Plant / Facility Location - State | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_LIQUID_VAPOR_RATE | VARCHAR2 | Process - Liquefaction/Vaporization Rate (MMCF/D) at the time of the Incident | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_NUM_VAPORIZERS | VARCHAR2 | Process - Number of Vaporizers in service at the time of the Incident | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_TOTAL_CAPACITY | VARCHAR2 | Process - Total Capacity (MMCF/D) | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_TRUCK_IND | VARCHAR2 | LNG Source - | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_RAILROAD_IND | VARCHAR2 | LNG Source - | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_MARINE_IND | VARCHAR2 | LNG Source - | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_LIQUEFY_IND | VARCHAR2 | LNG Source - | PART B – ADDITIONAL FACILITY INFORMATION
INTER_INTRA | VARCHAR2 | Interstate means the plant operates under a FERC certificate | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_NUMBER_TANKS | VARCHAR2 | LNG Storage - Number of LNG Tanks | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_VOLUME_STORAGE | VARCHAR2 | LNG Storage - Volume of LNG in Storage at the time of the Incident (Bbls) | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_BASE_LOAD_IND | NUMBER | Type of LNG Plant / Facility - Based Load | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_PEAK_SHAVE_IND | VARCHAR2 | Type of LNG Plant / Facility - Peak Shaving | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_SATELLITE_IND | VARCHAR2 | Type of LNG Plant / Facility - Satellite | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_MOBILE_TEMP_IND | VARCHAR2 | Type of LNG Plant / Facility - Mobile / Temporary | PART B – ADDITIONAL FACILITY INFORMATION
SUB_MOBILE_TEMP_INTRASTATE_IND | VARCHAR2 | Type of LNG Plant / Facility - Mobile / Temporary - InTRAstate | PART B – ADDITIONAL FACILITY INFORMATION
SUB_MOBILE_TEMP_INTERSTATE_IND | VARCHAR2 | Type of LNG Plant / Facility - Mobile / Temporary - InTERstate | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_OTHER_IND | VARCHAR2 | Type of LNG Plant / Facility - Other | PART B – ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_OTHER_DETAILS | VARCHAR2 | Type of LNG Plant / Facility - Other Details | PART B – ADDITIONAL FACILITY INFORMATION
FUNCTION_MARINE_TERMINAL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Marine Terminal | PART B – ADDITIONAL FACILITY INFORMATION
SUB_MARINE_IMPORT_TERMINAL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Marine Import Terminal | PART B – ADDITIONAL FACILITY INFORMATION
SUB_MARINE_EXPORT_TERMINAL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Marine Export Terminal | PART B – ADDITIONAL FACILITY INFORMATION
FUNCTION_STORAGE_IND | NUMBER | Function of LNG Plant / Facility at the time and date of the Incident - Storage | PART B – ADDITIONAL FACILITY INFORMATION
SUB_STORAGE_WITH_LIQUEFY_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Storage With Liquefaction | PART B – ADDITIONAL FACILITY INFORMATION
SUB_STORAGE_WO_LIQUEFY_IND | NUMBER | Function of LNG Plant / Facility at the time and date of the Incident - Storage Without Liquefaction | PART B – ADDITIONAL FACILITY INFORMATION
FUNCTION_STRANDED_UTILITY_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Stranded Utility | PART B – ADDITIONAL FACILITY INFORMATION
FUNCTION_VEHICULAR_FUEL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Vehicular Fuel | PART B – ADDITIONAL FACILITY INFORMATION
FUNCTION_NITRO_SPECIAL_USE_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Nitrogen Rejection Unit or Other Special Use | PART B – ADDITIONAL FACILITY INFORMATION
FUNCTION_SPECIAL_USE_DETAILS | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Nitrogen Rejection Unit or Other Special Use Details | PART B – ADDITIONAL FACILITY INFORMATION
ITEM_INVOLVED | VARCHAR2 | Item involved in Incident | PART B – ADDITIONAL FACILITY INFORMATION
ITEM_INVOLVED_DETAILS | VARCHAR2 | Item Involved in Incident Other - Details | PART B – ADDITIONAL FACILITY INFORMATION
EST_COST_OPER_PAID | NUMBER | Estimated Property Damage - Estimated cost of public and non-Operator private property damage | PART C – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OPER_PAID_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_PROP_DAMAGE | NUMBER | Estimated Property Damage - Estimated cost of Operator’s property damage & repairs | PART C – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_PROP_DAMAGE_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_EMERGENCY | NUMBER | Estimated Property Damage - Estimated cost of Operator’s emergency response | PART C – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_EMERGENCY_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_OTHER | NUMBER | Estimated Property Damage - Estimated other costs | PART C – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OTHER_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_OTHER_DETAILS | VARCHAR2 | Estimated Property Damage - Estimated other costs Specified | PART C – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_GAS_RELEASED | NUMBER | Estimated Property Damage - Estimated cost of commodity lost | PART C – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_GAS_RELEASED_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_INTENTIONAL_RELEASE | NUMBER | Estimated Property Damage - Estimated cost of commodity released during intentional and controlled blowdown | PART C – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_INTENT_REL_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
TOTAL_COST | NUMBER | Sum of EST_COST_OPER_PAID, EST_COST_PROP_DAMAGE, EST_COST_EMERGENCY, EST_COST_OTHER, EST_COST_GAS_RELEASED, and EST_COST_INTENTIONAL_RELEASE | Not on the form
TOTAL_COST_IN84 | Number | Converted Property Damage to 1984 dollars | Not on the form
TOTAL_COST_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
CCS_IN_PLACE_IND | NUMBER | Was a computerized Control System in place | PART D – ADDITIONAL OPERATING INFORMATION
CCS_OPERATING_IND | NUMBER | Computerized Control System in place - was it operating at the time of the Incident | PART D – ADDITIONAL OPERATING INFORMATION
CCS_FUNCTIONAL_IND | VARCHAR2 | Computerized Control System in place - Was it fully functional at the time of the Incident | PART D – ADDITIONAL OPERATING INFORMATION
ACCIDENT_IDENTIFIER | VARCHAR2 | How Incident was identified for the Operator | PART D – ADDITIONAL OPERATING INFORMATION
ACCIDENT_DETAILS | VARCHAR2 | How Incident was identified for the Operator - Other Details | PART D – ADDITIONAL OPERATING INFORMATION
EMPLOYEE_DRUG_TEST_IND | VARCHAR2 | Operator employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART E – DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_TESTED | NUMBER | Number of employees tested | PART E – DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_FAILED | VARCHAR2 | Number of employees failed | PART E – DRUG & ALCOHOL TESTING INFORMATION
CONTRACTOR_DRUG_TEST_IND | VARCHAR2 | Operator contractor employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART E – DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_TESTED | VARCHAR2 | Number of contractors tested | PART E – DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_FAILED | VARCHAR2 | Number of contractors failed | PART E – DRUG & ALCOHOL TESTING INFORMATION
CAUSE | VARCHAR2 | Apparent Cause of the Incident | PART F – APPARENT CAUSE
CAUSE_DETAILS | VARCHAR2 | Sub-Cause of Incident | PART F – APPARENT CAUSE
MAP_CAUSE | VARCHAR2 | Cause by PHMSA for 20 year Incident trending | Not on the form
MAP_SUBCAUSE | VARCHAR2 | SubCause by PHMSA for 20 year Incident trending | Not on the form
INTERNAL_EXTERNAL | VARCHAR2 | Corrosion Failure Sub-Cause (Internal, External) | PART F1 - Corrosion Failure
NATURAL_FORCE_TYPE | NUMBER | Natural Force Damage Sub-Cause | PART F2 - Natural Force Damage
NF_OTHER_DETAILS | VARCHAR2 | Natural Force Damage - Other Nat.Force Damage, or Sub-type Details | PART F2 - Natural Force Damage
PARTY_TYPE | VARCHAR2 | Excavation Damage Sub-Cause | PART F3 – Excavation Damage
OUTSIDE_FORCE_TYPE | VARCHAR2 | Other Outside Force Damage Sub-Cause | PART F4 - Other Outside Force Damage
OSF_VEHICLE_SUBTYPE | NUMBER | Other Outside Force Damage - Sub-cause Damage by Car, Truck, or Other Motorized Vehicle/Equipment NOT Engaged in Excavation - Vehicle/Equipment operated by | PART F4 - Other Outside Force Damage
OSF_HURRICANE_IND | VARCHAR2 | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Hurricane (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_TROPICAL_STORM_IND | VARCHAR2 | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Tropical Storm (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_TORNADO_IND | VARCHAR2 | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Tornado (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_HEAVY_RAINS_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Heavy Rains/Flood (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_OTHER_WEATHER_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Other type (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_OTHER_WEATHER_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Other type Details | PART F4 - Other Outside Force Damage
OSF_INTENTIONAL_SUBTYPE | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Specify | PART F4 - Other Outside Force Damage
OSF_INTENTIONAL_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Specify Other Details | PART F4 - Other Outside Force Damage
OSF_INTENT_SECURITY_BREACH_IND | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Specify - Did the Intentional Damage involve a breach of security | PART F4 - Other Outside Force Damage
OSF_OTHER_DETAILS | NUMBER | Other Outside Force Damage - Sub-cause Other Details | PART F4 - Other Outside Force Damage
PWJF_FIELD_EXAM_IND | NUMBER | Material Failure of Pipe or Weld - Based on Field Examination | PART F5 - Material Failure of Pipe or Weld
PWJF_METALLURGICAL_IND | VARCHAR2 | Material Failure of Pipe or Weld - Based on Determined by Metallurgical Analysis | PART F5 - Material Failure of Pipe or Weld
PWJF_OTHER_ANALYSIS_IND | VARCHAR2 | Material Failure of Pipe or Weld - Based on Other Analysis | PART F5 - Material Failure of Pipe or Weld
PWJF_STILL_UNDER_INVEST_IND | VARCHAR2 | Material Failure of Pipe or Weld - Sub-cause is Tentative or Suspected; Still Under Investigation | PART F5 - Material Failure of Pipe or Weld
PWJF_FAILURE_TYPE | VARCHAR2 | Material Failure of Pipe or Weld Sub-cause | PART F5 - Material Failure of Pipe or Weld
PWJF_INSULATION_DEGRAD_IND | VARCHAR2 | Material Failure of Pipe or Weld - Sub-cause Low temperature embrittlement - Was insulation degradation a factor in this failure | PART F5 - Material Failure of Pipe or Weld
EQ_FAILURE_TYPE | VARCHAR2 | Equipment Failure Sub-Cause | PART F6 - Equipment Failure
EQ_FAILURE_DETAILS | VARCHAR2 | Equipment Failure - Other Equipment Failure Details | PART F6 - Equipment Failure
EQ_LOW_TEMP_EMBRITTLEMENT_IND | VARCHAR2 | Equipment Failure - Did this failure involve Low Temperature Embrittlement due to process fluids | PART F6 - Equipment Failure
EQ_INSULATION_DEGRADATION_IND | VARCHAR2 | Equipment Failure - Was insulation degradation a factor in this failure | PART F6 - Equipment Failure
OPERATION_TYPE | VARCHAR2 | Incorrect Operation Sub-Cause | PART F7 - Incorrect Operation
OPERATION_DETAILS | VARCHAR2 | Incorrect Operation - Other Incorrect Operation Details | PART F7 - Incorrect Operation
RELATED_INADEQUATE_PROC_IND | VARCHAR2 | Incorrect Operation - Incident related to Inadequate procedure (Yes, Null) | PART F7 - Incorrect Operation
RELATED_NO_PROC_IND | VARCHAR2 | Incorrect Operation - Incident related to No procedure established (Yes, Null) | PART F7 - Incorrect Operation
RELATED_FAILURE_FOLLOW_IND | VARCHAR2 | Incorrect Operation - Incident related to Failure to follow procedure (Yes, Null) | PART F7 - Incorrect Operation
RELATED_OTHER_IND | VARCHAR2 | Incorrect Operation - Incident related to Other (Yes, Null) | PART F7 - Incorrect Operation
OPERATION_RELATED_DETAILS | VARCHAR2 | Incorrect Operation - Incident related to Other Details | PART F7 - Incorrect Operation
OTHER_TYPE | VARCHAR2 | Other Incident Cause Sub-Cause | PART F8 – Other Incident Cause
MISC_DETAILS | VARCHAR2 | Other Incident Cause - Miscellaneous Details | PART F8 – Other Incident Cause
UNKNOWN_SUBTYPE | VARCHAR2 | Other Incident Cause - Unknown Sub-type | PART F8 – Other Incident Cause
PREPARER_NAME | VARCHAR2 | Preparer's Name (Person filing the report) | PART H – PREPARER AND AUTHORIZED SIGNATURE
PREPARER_TITLE | NUMBER | Preparer's Title | PART H – PREPARER AND AUTHORIZED SIGNATURE
PREPARER_EMAIL | VARCHAR2 | Preparer's Email address | PART H – PREPARER AND AUTHORIZED SIGNATURE
PREPARER_TELEPHONE | VARCHAR2 | Preparer’s Telephone number | PART H – PREPARER AND AUTHORIZED SIGNATURE
PREPARER_FAX | VARCHAR2 | Preparer's Facsimile number | PART H – PREPARER AND AUTHORIZED SIGNATURE
PREPARED_DATE | VARCHAR2 | Date of filing | PART H – PREPARER AND AUTHORIZED SIGNATURE
AUTHORIZER_NAME | VARCHAR2 | Authorized Signature’s name | PART H – PREPARER AND AUTHORIZED SIGNATURE
AUTHORIZER_TITLE | VARCHAR2 | Authorized Title | PART H – PREPARER AND AUTHORIZED SIGNATURE
AUTHORIZER_TELEPHONE | VARCHAR2 | Authorized Telephone number | PART H – PREPARER AND AUTHORIZED SIGNATURE
AUTHORIZER_EMAIL | VARCHAR2 | Authorized Email address | PART H – PREPARER AND AUTHORIZED SIGNATURE
NARRATIVE | VARCHAR2 | Narrative | PART G – NARRATIVE DESCRIPTION OF THE INCIDENT

## lng2011toPresent
DATAFILE_AS_OF | SIGNIFICANT | SERIOUS | REPORT_NUMBER | SUPPLEMENTAL_NUMBER | REPORT_RECEIVED_DATE | REPORT_TYPE | OPERATOR_ID | NAME | OPERATOR_STREET_ADDRESS | OPERATOR_CITY_NAME | OPERATOR_STATE_ABBREVIATION | OPERATOR_POSTAL_CODE | LOCAL_DATETIME | IYEAR | NRC_RPT_NUM | NRC_RPT_DATETIME | UNINTENTIONAL_RELEASE_IND | INTENTIONAL_RELEASE_IND | EMERGENCY_SHUTDOWN_IND | RESULTED_FROM_OTHER_IND | RESULTED_FROM_OTHER_DETAILS | COMMODITY_RELEASED_TYPE | COMMODITY_DETAILS | UNINTENTIONAL_RELEASE | INTENTIONAL_RELEASE | VOLUME_TO_GROUND | FATALITY_IND | NUM_EMP_FATALITIES | NUM_CONTR_FATALITIES | NUM_ER_FATALITIES | NUM_GP_FATALITIES | FATAL | INJURY_IND | NUM_EMP_INJURIES | NUM_CONTR_INJURIES | NUM_ER_INJURIES | NUM_GP_INJURIES | INJURE | SHUTDOWN_DUE_ACCIDENT_IND | SHUTDOWN_EXPLAIN | SHUTDOWN_DATETIME | RESTART_DATETIME | STILL_SHUTDOWN_IND | IGNITE_IND | EXPLODE_IND | NUM_PUB_EVACUATED | NUM_OPER_AND_CONTRACTOR_EVAC | FACILITY_NAME | NPMS_LNG_ID | FACILITY_STATUS | FACILITY_LATITUDE | FACILITY_LONGITUDE | FACILITY_STATE | FACILITY_LIQUID_VAPOR_RATE | FACILITY_NUM_VAPORIZERS | FACILITY_TOTAL_CAPACITY | FACILITY_SOURCE_TRUCK_IND | FACILITY_SOURCE_RAILROAD_IND | FACILITY_SOURCE_MARINE_IND | FACILITY_SOURCE_LIQUEFY_IND | INTER_INTRA | FACILITY_NUMBER_TANKS | FACILITY_VOLUME_STORAGE | FACILITY_TYPE_BASE_LOAD_IND | FACILITY_TYPE_PEAK_SHAVE_IND | FACILITY_TYPE_SATELLITE_IND | FACILITY_TYPE_MOBILE_TEMP_IND | SUB_MOBILE_TEMP_INTRASTATE_IND | SUB_MOBILE_TEMP_INTERSTATE_IND | FACILITY_TYPE_OTHER_IND | FACILITY_TYPE_OTHER_DETAILS | FUNCTION_MARINE_TERMINAL_IND | SUB_MARINE_IMPORT_TERMINAL_IND | SUB_MARINE_EXPORT_TERMINAL_IND | FUNCTION_STORAGE_IND | SUB_STORAGE_WITH_LIQUEFY_IND | SUB_STORAGE_WO_LIQUEFY_IND | FUNCTION_STRANDED_UTILITY_IND | FUNCTION_VEHICULAR_FUEL_IND | FUNCTION_NITRO_SPECIAL_USE_IND | FUNCTION_SPECIAL_USE_DETAILS | ITEM_INVOLVED | ITEM_INVOLVED_DETAILS | EST_COST_OPER_PAID | EST_COST_OPER_PAID_CURRENT | EST_COST_PROP_DAMAGE | EST_COST_PROP_DAMAGE_CURRENT | EST_COST_EMERGENCY | EST_COST_EMERGENCY_CURRENT | EST_COST_OTHER | EST_COST_OTHER_CURRENT | EST_COST_OTHER_DETAILS | EST_COST_GAS_RELEASED | EST_COST_GAS_RELEASED_CURRENT | EST_COST_INTENTIONAL_RELEASE | EST_COST_INTENT_REL_CURRENT | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | CCS_IN_PLACE_IND | CCS_OPERATING_IND | CCS_FUNCTIONAL_IND | ACCIDENT_IDENTIFIER | ACCIDENT_DETAILS | EMPLOYEE_DRUG_TEST_IND | NUM_EMPLOYEES_TESTED | NUM_EMPLOYEES_FAILED | CONTRACTOR_DRUG_TEST_IND | NUM_CONTRACTORS_TESTED | NUM_CONTRACTORS_FAILED | CAUSE | CAUSE_DETAILS | MAP_CAUSE | MAP_SUBCAUSE | INTERNAL_EXTERNAL | NATURAL_FORCE_TYPE | NF_OTHER_DETAILS | PARTY_TYPE | OUTSIDE_FORCE_TYPE | OSF_VEHICLE_SUBTYPE | OSF_HURRICANE_IND | OSF_TROPICAL_STORM_IND | OSF_TORNADO_IND | OSF_HEAVY_RAINS_IND | OSF_OTHER_WEATHER_IND | OSF_OTHER_WEATHER_DETAILS | OSF_INTENTIONAL_SUBTYPE | OSF_INTENTIONAL_DETAILS | OSF_INTENT_SECURITY_BREACH_IND | OSF_OTHER_DETAILS | PWJF_FIELD_EXAM_IND | PWJF_METALLURGICAL_IND | PWJF_OTHER_ANALYSIS_IND | PWJF_STILL_UNDER_INVEST_IND | PWJF_FAILURE_TYPE | PWJF_INSULATION_DEGRAD_IND | EQ_FAILURE_TYPE | EQ_FAILURE_DETAILS | EQ_LOW_TEMP_EMBRITTLEMENT_IND | EQ_INSULATION_DEGRADATION_IND | OPERATION_TYPE | OPERATION_DETAILS | RELATED_INADEQUATE_PROC_IND | RELATED_NO_PROC_IND | RELATED_FAILURE_FOLLOW_IND | RELATED_OTHER_IND | OPERATION_RELATED_DETAILS | OTHER_TYPE | MISC_DETAILS | UNKNOWN_SUBTYPE | PREPARER_NAME | PREPARER_TITLE | PREPARER_EMAIL | PREPARER_TELEPHONE | PREPARER_FAX | PREPARED_DATE | AUTHORIZER_NAME | AUTHORIZER_TITLE | AUTHORIZER_TELEPHONE | AUTHORIZER_EMAIL | NARRATIVE
2016-12-30 10:54 | NO | NO | 20120001 | 15002 | 2012-11-28 12:27 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 220 N.W. SECOND AVENUE | PORTLAND | OR | 97209 | 2012-11-04 14:38 | 2012 | 1029623 | 2012-11-04 16:00 | NO | NO | YES | NO |  | OTHER COMMODITY | CO2 | 230 |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2012-11-04 14:38 | 2012-11-07 11:00 |  | NO | NO | 0 | 0 | NEWPORT LNG PLANT | NEWPORT | IN SERVICE | 44.62425232 | -124.0266953 | OR | 6 | 0 | 6 |  |  |  | YES | INTRASTATE | 1 | 165000 |  | YES | [9 empty] | YES | YES | [5 empty] | OTHER | Plant Control System | 0 | 0 | 10000 | 10468.2722 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 10000 | 5271.4067 | 10468.2722 | YES | YES | NO | OTHER | COMPUTERIZED CONTROL SYSTEM AND LOCAL OPERATING PERSONNEL. | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [22 empty] | OTHER EQUIPMENT FAILURE | PLANT CONTROL SYSTEM | NO | NO | [10 empty] | ANDREA SCOTT | COMPLIANCE SPECIALIST | a3s@nwnatural.com | 503-226-4211 |  | 2012-12-18 | KERRY SHAMPINE | MANAGER CODE COMPLIANCE | 503-226-4211 | kfs@nwnatural.com | ON SUNDAY NOVEMBER 4, 2012 AT APPROXIMATELY 2:30PM PST AN EVENT OCCURRED AT NW NATURAL¿S NEWPORT LNG STORAGE PLANT LOCATED AT 1702 YAQUINA BAY RD IN NEWPORT, OREGON. THE PLANT WAS OPERATING IN LIQUEFACTION MODE AND EXPERIENCED AN UNPLANNED SHUTDOWN OF ITS LIQUEFACTION PROCESS. ON-SITE PERSONNEL RESPONDED APPROPRIATELY AND RETURNED THE PLANT TO HOLD MODE AND VERIFIED SAFE CONDITIONS. THERE WAS A SMALL CYCLING RELEASE OF CO2 FROM A VESSEL THROUGH ITS RELIEF VALVE FOR A PERIOD OF ABOUT 20 MINUTES. FURTHER RESEARCH OVER THE NEXT 24 HOURS CONFIRMED THE PRIMARY CAUSE OF THE EVENT AS THE FAILURE OF AN ALLEN-BRADLEY PLC-5/40E PROCESSOR BOARD. THIS PLC WAS PROGRAMMED AS THE CONTROL PLC FOR THE PLANT LIQUEFACTION PROCESS. A REPLACEMENT PLC WAS PROCURED AND DELIVERED TO THE PLANT ON WEDNESDAY NOVEMBER 7, 2012. THE LIQUEFACTION PLC PROGRAM WAS RELOADED INTO THE NEW PROCESSOR AND ITS FUNCTIONALITY WAS VERIFIED THAT SAME DAY. THE PLANT WAS DECLARED BACK IN SERVICE BY NOON WEDNESDAY NOVEMBER 7, 2012.
2016-12-30 10:54 | NO | NO | 20140001 | 15015 | 2014-01-29 16:28 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2013-12-31 07:00 | 2013 | 1069801 | 2013-12-31 09:37 | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 1 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2013-12-31 07:05 |  | YES | YES | NO | 0 | 0 | Portable tanker and vaporizer |  | IN SERVICE |  |  | MN | 1025 | 1 | 6000 | YES |  |  |  | INTERSTATE | 2 | 234 |  |  |  | YES |  | YES | [8 empty] | YES |  |  |  | RELIEF VALVE |  | 0 | 0 | 1000 | 1028.9311 | 0 | 0 | 0 | 0 |  | 500 | 436.4754 | 0 | 0 | 1500 | 922.842 | 1465.4065 | NO |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [22 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | NO | NO | [10 empty] | JOHN GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  | 2016-04-25 | THOMAS CORRELL | DIRECTOR OF PIPELINE SAFETY | 402-398-7715 | thomas.correll@nngco.com | ON TUESDAY, DECEMBER 31, 2013 AT APPROXIMATELY 0700 CST A FLASH FIRE OCCURRED DURING LIQUIFIED NATURAL GAS DELIVERY OPERATIONS AT THE BENSON, MINNESOTA TOWN BORDER STATION. INFORMATION INDICATES THE CAUSE OF THE FLASH FIRE WAS A CATASTROPHIC FAILURE OF A FUEL RUN REGULATOR LOCATED ON THE VAPORIZER TRAILER. THE REGULATOR FAILURE CAUSED MULTIPLE RELIEF VALVES TO EXHAUST GAS TO THE ATMOSPHERE WHICH WAS IGNITED BY THE WATER/GLYCOL HEATER BURNERS LOCATED ON THE VAPORIZER TRAILER. TWO EMPLOYEES WERE EXAMINED AT A NEARBY HOSPITAL AND RELEASED BACK TO FULL DUTY. THEY BOTH HAD SUNBURN LIKE INJURIES. NORTHERN HAD PLACED THIS TEMPORARY / PORTABLE LNG TANKER AND VAPORIZER TAILER AT THE BENSON, MINNESOTA TOWN BORDER STATION AS A CONTINGENCY WHILE WORK WAS BEING CONDUCTED UPSTREAM AT THE ALEXANDRIA, MINNESOTA COMPRESSOR STATION. THE TANKER AND VAPORIZER HAD BEEN CONNECTED TO THE BENSON TOWN BORDER STATION SINCE 12/27/2013 BUT WASN'T IN-SERVICE UNTIL THE MORNING OF 12/31/2013. THE WATER BATH HEATERS ON THE VAPORIZER TRAILER WERE LIT BUT LNG WAS NOT BEING DELIVERED. ON 12/31/2013, THE PIPELINE GAS PRESSURE WAS LOW ENOUGH TO TEST THE LNG DELIVERY. THE DELIVERY WAS JUST BEGINNING TO COME ON WHEN THE REGULATOR FAILED AND THE FLASH FIRE OCCURRED. THE TOWN OF BENSON, MINNESOTA WAS NEVER IN DANGER OF LOSING NATURAL GAS SERVICE.
2016-12-30 10:54 | YES | YES | 20140002 | 15014 | 2014-05-06 15:12 | SUPPLEMENTAL FINAL | 39054 | WILLIAMS PARTNERS OPERATING LLC | ONE WILLIAMS CENTER | TULSA | OK | 74172 | 2014-03-31 08:19 | 2014 | 1078325 | 2014-03-31 09:23 | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 14000 | 154200 | 0 | NO |  |  |  |  | 0 | YES | 1 | 0 | 0 | 0 | 1 | YES |  | 2014-03-31 08:19 | 2016-03-15 08:15 |  | YES | YES | 150 | 18 | Plymouth LNG Peak Shaving Plant |  | IN SERVICE |  |  | WA | 0 | 0 | 300 |  |  |  | YES | INTERSTATE | 2 | 344309 |  | YES | [9 empty] | YES | YES | [5 empty] | IN-PLANT PIPING |  | 71300 | 72263.1569 | 40790000 | 41341012.2132 | 190000 | 192566.6173 | 4698000 | 4761462.9904 | Purification system upgrade, certain MI inspections and enviro monitoring. | 80960 | 60400.9807 | 672800 | 501948.8616 | 46503060 | 23870163.6811 | 46929654.8202 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | YES | 16 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [26 empty] | OTHER INCORRECT OPERATION | INADEQUATE PURGE FOLLOWING MAINTENANCE ACTIVITIES. | YES | [7 empty] | JARED ELLSWORTH | MANAGER PIPELINE SAFETY | jared.ellsworth@williams.com | 8015846539 |  | 2016-03-25 | JARED ELLSWORTH | MANAGER PIPELINE SAFETY | 8015846539 | jared.ellsworth@williams.com | AT APPROXIMATELY 08:19 PDT THE PLYMOUTH LNG FACILITY EXPERIENCED AN INTERNAL DETONATION RESULTING IN RAPID OVERPRESSURE AND SUBSEQUENT FAILURE OF PORTIONS OF THE LNG1 PURIFICATION AND REGENERATION SYSTEM, INCLUDING IN PLANT PIPING AND AN ADSORBER VESSEL, CAUSING DAMAGE TO ADJACENT BUILDINGS AND EQUIPMENT. DEBRIS FROM THE RUPTURE PENETRATED THE OUTER WALL OF ONE OF TWO LNG STORAGE TANKS. NATURAL GAS VENTED FROM THE VAPOR SPACE BETWEEN THE INNER AND OUTER WALLS OF THE STORAGE TANK BUT DID NOT IGNITE. STATION PERSONNEL IMMEDIATELY EXECUTED AN ESD OF THE FACILITY. OF 5 EMPLOYEES TAKEN TO THE HOSPITAL FOR EVALUATION, 4 EMPLOYEES WERE TREATED AND RELEASED AND 1 EMPLOYEE WAS ADMITTED FOR BURN INJURIES AND RELEASED SEVERAL DAYS LATER. A THIRD PARTY INVESTIGATION FIRM WAS CONTRACTED TO DOCUMENT THE INCIDENT LOCATION AND MANAGE ALL EVIDENCE. VARIOUS CONSULTANTS WERE ENGAGED IN THE COMPLETION OF AN INCIDENT INVESTIGATION. THE INVESTIGATION DETERMINED THE LEADING CAUSE WAS THE PRESENCE OF A FUEL/AIR MIXTURE REMAINING IN THE SYSTEM FOLLOWING MAINTENANCE ACTIVITIES. THE FUEL/AIR MIX THEN AUTO-IGNITED WITHIN THE SYSTEM PIPING UPON STARTUP WHEN THE FLAMMABLE MIXTURE ENTERED THE INLET OF A SALT BATH HEATER.
2016-12-30 10:54 | NO | NO | 20140003 | 15005 | 2014-08-19 08:14 | ORIGNAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS CO | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2014-07-27 19:00 | 2014 | 1090405 | 2014-07-27 21:57 | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 1 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2014-07-27 19:00 | 2014-07-27 20:20 |  | NO | NO | 0 | 0 | Kingsport LNG Plant | Kingsport LNG | IN SERVICE | 36.44537113 | -82.52234253 | TN | 0 | 0 | 348000 |  |  |  | YES | INTERSTATE | 1 | 252000 |  | YES | [9 empty] | YES | YES | [5 empty] | RELIEF VALVE |  | 0 | 0 | 84500 | 85641.4693 | 0 | 0 | 0 | 0 |  | 4 | 2.9842 | 0 | 0 | 84504 | 43128.4147 | 85644.4535 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS |  | HIGH WINDS | [34 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 | 2014-08-19 | RICK KIVELA | DIRECTOR OPERATION COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | AFTER A TORNADO DISRUPTED ELECTRIC POWER TRANSMISSION TO THE EAST TENNESSEE LNG FACILITY IN KINGSPORT, TENNESSEE, THE GENERATOR AT THE FACILITY DID NOT IMMEDIATELY ACTIVATE. THE COMPRESSOR STOPPED WHICH CAUSED PRESSURE TO RISE IN THE LNG TANK AND NATURAL GAS VENTED THROUGH THE ASSOCIATED RELIEF VALVE UNTIL THE GENERATOR SWITCHED ON AND COMPRESSOR RETURNED TO SERVICE.
2016-12-30 10:54 | YES | NO | 20150001 | 15017 | 2015-02-13 18:32 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD (POB 7608, 83707) | BOISE | ID | 83709 | 2014-12-18 12:30 | 2014 | DO NOT KNOW NRC REPORT NUMBER |  | YES | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 185 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2014-12-18 01:30 |  | YES | NO | NO | 0 | 0 | NAMPA LNG FACILITY | NAMPA LNG | IN SERVICE |  |  | ID | 5 | 0 | 5 |  |  |  | YES | INTRASTATE | 1 | 94000 |  | YES | [9 empty] | YES | YES |  |  | YES |  |  | WELD |  | 0 | 0 | 100000 | 101350.8512 | 300 | 304.0526 | 2000 | 2027.017 | crane to remove Economizer and Company labor | 555 | 414.063 | 0 | 0 | 102855 | 52594.0353 | 104095.9838 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [16 empty] | YES |  |  |  | CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | [15 empty] | CRAIG CHAPIN | DIRECTOR - ENGINEERING SERVICES | craig.chapin@intgas.com | 208-377-6142 |  | 2016-09-21 | CRAIG CHAPIN | DIRECTOR - ENGINEERING SERVICES | 208-377-6142 | craig.chapin@intgas.com | A WELD ON ONE OF THE TUBES WITHIN THE ECONOMIZER FAILED (PULLED APART) LEAKING ~ 600 PSIG METHANE GAS INTO THE ENCLOSED AREA OF THE ECONOMIZER. BOXED AREA OF ECONOMIZER FILLED WITH GAS AND RUPTURED RESULTING IN DAMAGE TO THE TOP AND SIDE OF THE BOX. THE LEAKING GAS RESULTED IN A LOW PRESSURE ALARM ON THE CO2 PURIFICATION TOWER. OPERATORS ARRIVED ON SITE AND ACTIVATED THE LIQUEFACTION EMERGENCY SHUTDOWN. IT SHOULD BE NOTED A SRC REPORT WAS FILED ON 12-23-14 IN LIEU OF AN INCIDENT REPORT GIVEN THE INFORMATION AND SITUATION AT THAT TIME. THIS INCIDENT REPORT IS BEING SUBMITTED AT THIS TIME IN ADDITION TO THE SCR REPORT BASED ON THE RECOMMENDATION OF OUR IDAHO PUC REGULATOR. MONTHLY REPORTS ARE BEING SUBMITTED TO JERRY KENERSON AT JERRY.KENERSON@DOT.GOV PROVIDING UPDATED INFORMATION AS A NEW ECONOMIZER IS BEING BUILT AND INSTALLED.
2016-12-30 10:54 | NO | NO | 20150002 | 15008 | 2015-02-20 15:44 | SUPPLEMENTAL FINAL | 32206 | FREEPORT LNG DEVELOPMENT, L.P. | 333 CLAY STREET SUITE 5050 | HOUSTON | TX | 77002 | 2015-02-19 09:17 | 2015 | 1108577 | 2015-02-20 08:22 | YES | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 1711 |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2015-02-19 09:19 | 2015-02-19 11:51 |  | NO | NO | 0 | 50 | FREEPORT LNG DEVELOPMENT L.P. | 1 | IN SERVICE |  |  | TX | 0 | 0 | 1800 |  |  | YES |  | INTERSTATE | 2 | 160000 | YES | [7 empty] | YES | YES | YES | [7 empty] | FLANGE/GASKET |  | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 0 |  | 4771 | 4771 | 0 | 0 | 4796 | 4436.4036 | 4796 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [22 empty] | OTHER EQUIPMENT FAILURE | FLANGE GASKET ON A 4" PROCESS PIPELINE FAILED UNDER PRESSURE DURING MAINTENANCE / TESTING OF A VALVE UPSTREAM. | NO | NO | [10 empty] | MICHAEL STEPHENSON | REGULATORY COMPLIANCE SPECIALIST | mstephenson@freeportlng.com | 979-415-8728 | 979-415-8733 | 2015-02-20 | MICHAEL JOHNS | DIRECTOR REGUALTORY AFFAIRS | 979-415-8720 | mjohns@freeportlng.com | WHILE CONDUCTING VALVE TESTING / MAINTENANCE ON A PRESSURIZED NATURAL GAS LINE ~ 1100 PSI OF PRESSURE WAS RELEASED FROM A FAILED FLANGE GASKET THAT WAS POSITIONED BEHIND A BLIND FLANGE ON A PLANT NATURAL GAS HANDLING SYSTEM. THERE WERE NO PERSONNEL IN THE IMMEDIATE VICINITY OF THE RELEASE AND THE SYSTEM WAS SHUT DOWN IMMEDIATELY BY OPERATIONS BY UTILIZING AND ESD (EMERGENCY SHUT DOWN) BUTTON PULL STATION. NO INJURIES OCCURRED. THE IN-PLANT ALARM SYSTEM FUNCTIONED BY SOUNDING GAS RELEASE AND EVACUATION ALARMS AND ALL PERSONNEL LEFT THE AREA AND MUSTERED IN DESIGNATED LOCATIONS UNTIL THE SITUATION STABILIZED AND THE ALL-CLEAR HORN WAS SOUNDED. THE FLANGE WAS INSPECTED AND FOUND TO BE IN GOOD ORDER, THE GASKET WAS REPLACED AND THE SYSTEM WAS PUT BACK INTO SERVICE ON THE SAME DAY. REPORTS WERE FILED OR NOTIFICATIONS WERE MADE WITH FERC, NRC, PHMSA, BRAZORIA COUNTY COMMUNITY AWARENESS AND ENVIRONMENTAL RESPONSE AND THE CITY OF QUINTANA.
2016-12-30 10:54 | NO | NO | 20150004 | 15012 | 2015-12-30 12:39 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 220 N.W. SECOND AVENUE | PORTLAND | OR | 97209 | 2015-12-13 08:45 | 2015 | 1135692 | 2015-12-13 11:08 | NO | NO | YES | NO |  | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2015-12-13 08:54 | 2015-12-13 10:12 |  | NO | NO | 0 | 0 | GASCO LNG PLANT | GASCO | IN SERVICE |  |  | OR | 120 | 3 | 120 |  |  |  | YES | INTRASTATE | 1 | 106750 |  | YES | [9 empty] | YES | YES | [5 empty] | EMERGENCY SHUT-OFF VALVE (ESV) |  | 0 | 0 | 22829 | 22829 | 5000 | 5000 | 0 | 0 |  | 0 | 0 | 0 | 0 | 27829 | 14013.5808 | 27829 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION |  |  |  |  | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [30 empty] | SAMANTHA BURT | CODE COMPLIANCE SPECIALIST | s7b@nwnatural.com | 5032264211 |  | 2016-01-05 | JOE S. KARNEY | SENIOR MANAGER CODE COMPLIANCE | 5032264211 | jsk@nwnatural.com | AT APPROXIMATELY 8:49AM ON DECEMBER 13TH, 2015 NW NATURAL WAS NOTIFIED OF A SIGNIFICANT FIRE CLOSE TO THE PORTLAND LNG PLANT LOCATED AT 7900 NW SAINT HELENS RD., IN PORTLAND. A SEMI-TRUCK WITH A TANKER FULL OF FUEL TRAVELED OFF HIGHWAY 30 COLLIDING WITH A RAIL CAR CAUSING THE FIRE IMMEDIATELY ADJACENT TO THE PROPERTY. THE VEHICLE FIRE DISRUPTED THE PRIMARY POWER TO THE FACILITY WHICH RESULTED IN THE ACTIVATION OF THE ESD AT APPROXIMATELY 8:54AM. NWN FIRST RESPONDER ARRIVED ON SITE AT 10:12AM AND ACTIVATED BACK UP POWER. MINOR DAMAGE WAS EXPERIENCED AT THE CONTROL ROOM BUILDING DUE TO THE FIRE. NONE OF THE CRITICAL INFRASTRUCTURE OR OPERATIONAL SYSTEMS OF THE LNG PLANT WAS DAMAGED. PORTLAND GENERAL ELECTRIC REPAIRED THE PRIMARY POWER DECEMBER 15, 2015 AT 1:00PM. NW NATURAL IS REPORTING THE INCIDENT DUE TO LNG EMERGENCY SHUT DOWN.
2016-12-30 10:54 | NO | NO | 20160001 | 15016 | 2016-06-24 08:57 | ORIGNAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2016-04-20 11:59 | 2016 | 1145755 | 2016-04-20 12:45 | NO | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 325.2 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2016-04-20 11:59 | 2016-04-27 09:15 |  | NO | NO | 0 | 0 | LNG PLANT | 14 | IN SERVICE |  |  | IL | 10 | 0 | 10 |  |  |  | YES | INTRASTATE | 2 | 313358 |  | YES | [9 empty] | YES | YES | [5 empty] | IN-PLANT PIPING |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 823 | 823 | 0 | 0 | 823 | 763.1103 | 823 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN A TANK, VESSEL, OR SUMP/SEPARATOR OVERFLOW OR FACILITY OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [26 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN A TANK, VESSEL, OR SUMP/SEPARATOR OVERFLOW OR FACILITY OVERPRESSURE |  |  | YES | [6 empty] | SHAWN BARTELS | COMPLIANCE SPECIALIST | srbartels@peoplesgasdelivery.com | 312-240-5421 |  | 2016-06-24 | TOM WEBB | COMPLIANCE MANAGER | 312-240-4650 | tjwebb@peoplesgasdelivery.com | VALVE CONFIGURATION ON A TRANSMISSION LINE OUTSIDE OF THE LNG PLANT WAS CHANGED TO INCREASE FLOW IN THE PIPELINE WHICH THE LNG OUTLET ALSO FED INTO. AN INCREASE IN PRESSURE THAT ACCOMPANIED THE INCREASE IN FLOW IN THE PIPELINE CAUSED THE OUTLET OF THE LNG PLANT TO BACK UP, LIFTING RELIEF VALVES WITHIN THE LNG PLANT. TIMELINE: 11:30 AM: STATION VALVE RECONFIGURATION BEGINS IN AN ATTEMPT TO MITIGATE THE FROST HEAVING 11:55 AM: MAHOMET LINE #2 PRESSURE BEGINS TO INCREASE DUE TO VALVES 354 AND 471 BEING LEFT OPEN DURING THE RECONFIGURATION 11:59 AM: LNG FACILITY RELIEF VALVES BEGIN TO OPEN 11:59 AM: LNG FACILITY EMERGENCY SHUT DOWN SYSTEM ACTIVATED 12:06 PM: LNG ESD ALARM CLEARED 12:25 PM: PLANT MANAGER NOTIFIED OF INCIDENT 12:45 PM: NATIONAL RESPONSE CENTER NOTIFIED AND NRC REPORT #1145755 GENERATED 12:57 PM: ILLINOIS COMMERCE COMMISSION NOTIFIED 1:43 PM: ESTIMATED GAS RELEASE CALCULATED TO BE 325,200 SCF 3:10 PM: SHIFT OPERATOR AND ASSISTANT SHIFT OPERATOR SENT FOR POST-INCIDENT DRUG AND ALCOHOL TESTING 3:20 PM: RANDY STEWART WITH ICC ARRIVED AT MANLOVE FIELD FOR INVESTIGATION PGL CONSIDERS THIS INCIDENT CLOSED, BUT WILL REPORT QUARTERLY ON IT UNTIL ALL THE ICC AND PHMSA QUESTIONS HAVE BEEN ANSWERED.